## Slide 1
This material is protected by copyright law. The marks, Air Hygiene International, Inc. (AHI) and Air Hygiene University (AHU), along with their respective logos, are protected by trademark law. The material and the marks are the exclusive property of Air Hygiene International. All rights reserved.
CiSCO CEMS
USER GROUP
Keys to a
Successful RATA
Paul Little, QSTI (I-IV)
Director of Customer Service
(918) 289-6378
plittle@airhygiene.com
Air Hygiene International, Inc.
1600 W Tacoma Street
Broken Arrow, Oklahoma
(918) 307-8865
© 2012, 2013 Air Hygiene International, Inc.
Notes: Introduce yourself

## Slide 2
Objectives
Share a Written Standard
Present Air Hygiene’s approach to Relative Accuracy Test Audits (RATAs)
Discuss Services and Options (that could be advantageous)
1
Notes: Setup the Continuous Improvement Structure

## Slide 3
Checklist
Pre-mob
Setup
Test Day
Post Test / Before Demobilization
Report Review
2
Notes: Setup the Continuous Improvement Structure

## Slide 4
Before we Mobilize
Protocol
Unit specific info
3

## Slide 5
What does “Normal” mean?
4
Notes: But do you know where this comes from?

## Slide 6
Setup
Time Synchronization
CEMS makes, models, serial numbers
How long is it going to take?
Are we going to pass?
5
Notes: Encyclopedia Set

## Slide 7
What if we don’t agree?
Work systematically
Work from least to most evasive
  Stack inspection
    Is the CEMS probe there?
    Is the RM probe off-gassing?
  Sample lines
    Are all lines heating
    To what temperature(s)
  Leak checks
6
Notes: Encyclopedia Set

## Slide 8
What if we don’t agree?
(continued)
  Re-calibrations
    Try system mode for RM?
  What’s the parameter
    NOx
      How does the NO compare
      Now does the NO2 compare
      Run a CEMS NO2 conv. check
  Re-calibrations with shared gases
  Tap into each others sample lines
7
Notes: Encyclopedia Set

## Slide 9
Test Day
CEMS Calibration
How long is it going to take?
Are we going to pass?
  Stratification test can confirm
Everything included in a post-test review is something you’ll wish you would have asked pre-test
8
Notes: Encyclopedia Set

## Slide 10
Questions to Ask
Load
  Stable / Normal / Sec. Normal
Primary fuel combusted?
Correct point or points [Strat]
NO2 Conv efficiency ≥90%
Did the RATA pass
Is there a BAF
Was the tester a QI / QSTI
Was the company an AETB
9
Notes: Encyclopedia Set

## Slide 11
Questions to Ask
(continued)
Did all systems (CEMS and RM) pass calibrations
Did RM runs follow proper QA
Did RATA run times match
Were both CEMS and RM wet or dry
Did the RATA use nine runs
Was each RATA run 21 minutes
10
Notes: Encyclopedia Set

## Slide 12
Let ECMPS Do It
11

## Slide 13
Let ECMPS Do It
(continued)
12

## Slide 14
Let ECMPS Do It
(continued)
13

## Slide 15
Let ECMPS Do It
(continued)
14

## Slide 16
XML Code – Import and Eval
15

## Slide 17
Outcomes
16
Four RATAs conducted at the wrong test loads
Several RATAs reported at wrong load (i.e. CT plus ½ steam turbine)
A few RATAs ±9 test runs

## Slide 18
Advantages
17
Real time feedback
Captures our Field Manager’s “in the moment”
Corrective actions prior to demobilization

## Slide 19
The Future… is now
18
Same type of “robotic” check system utilized for the report

## Slide 20
Services and Options
19
XML / JSON Code
RA Calculations
  https://www.airhygiene.com/store/Air-Hygiene-Carbon-Emissions-Calculator-Tools.aspx

## Slide 21
Services and Options
20
Stack Testing
  Temporary CEMS
  Parts (i.e. Lines and Analyzers)
Cylinder Rental
Air Hygiene University

## Slide 22
Questions, Comments, Concerns?