## Slide 1: CALIBRATION CHECKS
Presenters:
Clif Petersen – Senior PLC Programmer
Reggie Williams – Environmental Scientist
09/14/2022

## Slide 2: How Does Software Validate the Hour
At least 1 valid minute in each of the 15-minute quadrants of each hour.
For hours of calibration or maintenance:
  2 valid minutes at least 15 minutes apart.
Minimize downtime:
  Allow a valid minute in the quadrant before starting calibration or maintenance.
  Schedule long tests; linearity, across the top of the hour.

## Slide 3: Hour with Quadrants

## Slide 4: Sequencing of the Calibration Gases

## Slide 5: Calibration Timing and Settings
Time of injection is primarily the time it takes for the gas to move through the probe to the analyzer.
Avoid high concentration followed by a lower or zero concentration.
O2 is easier to zero or span than other analyzers.

## Slide 6: TIME
PARAMETER | 40 CFR 60 | 40 CFR 75
7-Day Drift | Approximately 24-hours | Approximately 24-hours (UOD)
Daily Calibration |  | 24 + 2 clock hours
 |  | 24 + 2 UOH hours
Start-up |  | 8-hour grace period

## Slide 7: Late or Expired Cals
PARAMETER | 40 CFR 60 | 40 CFR 75
7-Day Drift | Must meet 40 CFR 60, App. B criteria to pass | Must meet 40 CFR 75, App. A criteria to pass
Daily Calibration | Not addressed. EPA v. State | Regulations require data invalidation

## Slide 8: Fail Limits
PARAMETER | 40 CFR 60 | 40 CFR 75
7-Day Drift | 1 X Appendix B, PS | 1 X Appendix A, PS or MD
Daily Calibration | 2 X PS – Once (Warning) | 2 X PS – Once (OOC) or MD
 | 2 X PS – 5 times (OOC) | 
 | 4 X PS- Once (OOC) Fails backwards | 

## Slide 9: Operational Status
PARAMETER | 40 CFR 60 | 40 CFR 75
7-Day Drift | Online | Online
 |  | ≤ 50 ppm exempt
Daily Calibration | Online & Offline | Online
 |  | Online & Offline, if determination test performed

## Slide 10: Dual Range Analyzers
PARAMETER | 40 CFR 60 | 40 CFR 75
7-Day Drift | Both ranges must pass, or analyzer is OOC (Guidance) | If one range fails, then analyzer is OOC (Regulation)
Daily Calibration | Online & Offline | Online
 |  | Online & Offline, if determination test performed

## Slide 11: Calibration Drift Gas Concentrations
PARAMETER | 40 CFR 60 | 40 CFR 75
Calibration | Zero (0 -20%) & High (50 -100%) | Zero (0 -20%) & Mid (50 -60%) or High (80 -100%)

## Slide 12: Instrument Air Usage
PARAMETER | 40 CFR 60 | 40 CFR 75
7-Day Drift | Not addressed in regulations, guidance or determinations | Allowed, but must demonstrate clean of O2 interferents
Daily Calibration | Online & Offline | Online

## Slide 13: Non-Test Errors e.g. Calibrating with cylinders turned off
PARAMETER | 40 CFR 60 | 40 CFR 75
7-Day Drift | Must meet 40 CFR 60, App. B criteria to pass | Does not affect test if a calibration was performed on the same day
Daily Calibration | Not addressed. EPA v. State | Non-test has no impact and should not be reported

## Slide 14: Questions?
THE END