## Slide 1: Part 75 Overview CiSCO CEMS Users Group Meeting September 2022

## Slide 2: Where do I find part 75?
All parts referenced within part 75 are found in Title 40 of the Code of Federal Regulations (CFR)
Within part 75 Title 40 CFR, part 60 Appendices A (test methods) and B (certain location and performance specifications), and part 72 (definitions) are referenced
https://www.ecfr.gov

## Slide 3: For Part 75 key definitions, refer to 40 CFR 72.2
Calibration gas
Continuous emissions monitoring systems (CEMS)
Diluent cap
EPA Protocol Gas
QA operating quarter
Unit operating hour
Zero air material

## Slide 4: What is the purpose of Part 75? Subpart A, General
Part 75 establishes the monitoring, recordkeeping, and reporting requirements for the Acid Rain Program
Subpart A (§§75.1-75.8) defines the purpose of the regulation and the extent of its applicability. Subpart A also includes general Acid Rain Program provisions, compliance dates, prohibitions
Acid Rain applicability provisions are found in §72.6

## Slide 5: What is the purpose of Part 75? Subpart A, General
In general, Part 75 was intended for utility owned boilers and combustion turbines serving electrical generators with a rated capacity of greater than 25 MW, selling electricity to the grid (refer to 40 CFR 72.6)
Part 75 was originally created to require sources to monitor, report, and keep records on SO2 (lb/hr), NOX (lb/mmBtu), and CO2 (tons/hr) emissions (e.g. Acid Rain Program)
Subpart H of Part 75 was later added for NOX (lb/hr) reporting (e.g. Cross State Air Pollution Rule (CSAPR))

## Slide 6: Compliance Dates, refer to 40 CFR 75.4
Certification of all Part 75 monitoring systems must be completed within 180 calendar days after a new unit commences commercial operation
A newly affected unit must also certify all Part 75 monitoring systems within 180 calendar days after the date on which the unit becomes affected
Certification must be completed on all monitoring systems within 90-unit operating days or 180 calendar days after emissions exhaust through a new stack or reagent is injected into a newly installed flue gas desulfurization control device or add-on NOX controls

## Slide 7: Subpart B, General Operating Requirements
Subpart B (§§75.10–75.19) presents the general emission monitoring requirements for each pollutant (SO2, NOX, etc.)
Special instructions are given for monitoring at common stack and multiple stack exhaust configurations

## Slide 8: General Operating Requirements, refer to 40 CFR 75.10
Monitoring systems are required to be in operation and monitoring anytime a unit combusts any fuel (refer to §75.10(d))
  Limited exceptions for quality assurance activities and when firing very low sulfur fuel
Minimum data capture requirements are found in §75.10(d)(1)

## Slide 9: Low Mass Emitter (LME)Monitoring Methodology, refer to 40 CFR 75.19
LME is an excepted monitoring methodology using a simplified conservative approach to determine all applicable Part 75 pollutants (SO2 (lb/hr), NOX (lb/mmBtu) and CO2 (tons/hr)) , heat input (mmBtu/hr), and operating parameters
LME is limited to gas and oil-fired units only that emit less than 25 tons of SO2 and 100 tons of NOX annually, and 50 tons of NOX during the ozone season
Emissions are determined using either default emission rate values found in tables, or a unit-and-fuel-specific emission rate based on testing, historical data, etc.

## Slide 10: Subpart C, Monitoring Operation and Maintenance Requirements
Subpart C (§§75.20-75.24) presents the process for certification and recertification of the required continuous monitoring systems, provides the quality assurance and quality control (QA/QC) requirements for the systems, specifies “out-of-control” periods, and requires bias adjustment of data from SO2, NOX, and flow monitors

## Slide 11: Initial Certification and Recertification Procedures, refer to 40 CFR 75.20
  75.20(a), initial certification is required at locations where Part 75 monitoring systems were never previously certified
  75.20(b), recertification is required whenever a change is made to a CEMS that significantly affects the ability to accurately measure or record emissions (e.g., an analyzer replacement)
  Conditional data provisions allow data to be conditionally validated during the recertification process
  Procedures for both initial and recertification are found in 72.20(c) specifying each required test (e.g. RATA, linearity check, 7-day drift, cycle time, and bias)

## Slide 12: Reference Test Methods and CEM Installation Requirements
Part 75 generally refers to reference test methods found in Appendix A of 40 CFR 60 with notable exceptions (refer to 40 CFR 75.22)
Install gas monitors at a location where the pollutant concentration and emission rate measurements are directly representative of the total emissions from the affected unit, following the procedures in section 8.1.1 of Performance Specification 2 in appendix B to part 60 (refer to 40 CFR 75 Appendix A paragraph 1.1)
Install volumetric flow monitors at a location that provides representative volumetric flow over all operating conditions (refer to 40 CFR 75 Appendix A paragraph 1.2)

## Slide 13: Subpart D, Missing Data Procedures
(§§75.30-37) describes the missing data procedures that are used to determine the appropriate substitute data values, for unit operating hours in which the monitoring systems fail to provide quality-assured data
For more information on missing data usage see the Monitoring Insights paper at the following link:
  https://www.epa.gov/sites/production/files/2021-03/documents/monitoring_insights_substitute_data.pdf

## Slide 14: Missing Data Substitution Procedures
Substitute data is used to ensure emissions are not under reported during periods when a CEMS is unavailable either as the result of QA or maintenance activities or failure to conduct or pass a QA test within the specified timeframe or limits
Specifies the algorithms to use for initial and standard missing data

## Slide 15: Missing Data Substitution Procedures
Missing data uses historical data in certain lookback periods and maximum values as required
Percent monitor data availability (PMA) is calculated on a monitored system (e.g. SO2 ppm) or calculated system (e.g. NOX lb/mmBtu) basis and used to determine which algorithm to use when determining an hourly substitute data value (refer to §75.32)
Missing values for some parameters (e.g. NOX (lb/mmBtu), volumetric stack flow (scfh)) are determined using historical lookback periods grouped by load bins, while others (e.g. SO2 (ppm), CO2 (%)) use historical lookback periods without load bin groupings

## Slide 16: Subpart E, Alternative Monitoring Systems
§§75.40-75.48 describes the requirements that must be met for approval of an alternative monitoring system
Parametric emission monitoring systems (PEMS)
Use of PEMS requires approval via the petition process specified in §75.66

## Slide 17: Subpart F, Recordkeeping Requirements
§§75.50-75.59 contains the recordkeeping requirements
  Monitoring plan
  Hourly operating and control parameter data
  Emissions
  Certification, quality assurance and quality control tests

## Slide 18: Subpart G, Reporting Requirements
§§75.60-75.67 contains the reporting requirements. Instructions are provided for submitting notifications, monitoring plans, certification applications, emissions reports, and special petitions to the Administrator
  Notifications (refer to §75.61)
  Petitions (refer to §75.66)
Part 75 submissions must be made by a Designated Representative, an alternate, or an assigned agent

## Slide 19: Subpart H, NOx Mass Emissions
§§75.70-75.75 describes the NOX mass emission monitoring requirements for sources in NOX mass emissions reduction programs that adopt Part 75, such as the annual and ozone season NOX trading programs under the CSAPR rule. Special instructions are provided for sources that report data only during the ozone season

## Slide 20: Appendix A ,Specification and CEM Test Procedures
Appendix A describes CEMS installation and certification test procedures, and provides performance specifications for the CEMS and explains how to set the span and range of CEMS
Discusses requirements to periodically reevaluate the appropriateness of span, range, maximum concentration defaults, etc.
Discusses gas RATA test procedures, including stratification testing and acceptance criteria

## Slide 21: Appendix B, Ongoing CEM Test Requirements
Appendix B describes the required on-going CEMS quality assurance tests and procedures, and includes rules for data validation
Identifies minimum QA/QC plan procedures and records requirements for CEMS, Appendix D, and Appendix E monitoring methods
Grace periods
Provides prescriptive data validation procedures
Requires quarterly volumetric stack flow to load tests
Discusses potential options for reduced volumetric stack flow RATA testing and how to conduct a load range analysis prior to gas and flow RATAs

## Slide 22: Appendix C, Missing Data Estimation Procedures
Appendix C provides guidelines for parametric and load-based missing data substitution
Specifies how load bins are determined for unit level and common stack level reporting

## Slide 23: Appendix D, Optional SO2 Methodology
Gas- and oil-fired units only
Determination of SO2 (lb/hr) and heat input (mmBtu/hr)
Requires fuel flow meters in conjunction with periodic sampling for sulfur and gross calorific value (GCV)
Discusses how to apply fuel sampling results
Data substitution procedures

## Slide 24: Appendix E, Optional NOX Methodology
Gas- and oil-fired peaking units only
Peaking units only as defined in 72.2
Also requires use of Appendix D
Requires periodic stack testing to determine NOX emission rates at four evenly spaced load levels correlated to heat input
Retest once every 20 calendar quarters
No grace periods
Simplified data substitution

## Slide 25: Appendix F, Equations and F-Factors
Appendix F provides equations for converting raw monitoring data into the appropriate units of measure
F-factor table
Diluent cap procedures

## Slide 26: Appendix G, Calculating and Estimating CO2 Emissions
Appendix G gives procedures for estimating and calculating CO2 mass emissions
Most gas and oil-fired units use equation G-4 to determine CO2 (tons/hr) emissions
Note that coal units use equation F-11 found in Appendix F to calculate CO2 (tons/hr) emissions

## Slide 27: Questions?
Question’s
Contact Information:
frushour.charles@epa.gov
202-343-9847